# LHC MAGNET QUENCH SCENARIOS

# Use Case Model

# This model will contain all use cases related to magnet quench situations in the LHC machine

# LHC Dipole Magnet Quench Use Case

### 1. Use Case Description

## USE CASE ID

| USE CASE NAME | LHC Dipole Magnet Quench | ID | #1 |
| --- | --- | --- | --- |
| USE CASE GROUP | LHC Magnet Quenches | PRIORITY | High |
| VERSION | 1.1 | DATE | 02/11/1999 |
| REASON FOR CHANGE | New |
| PREPARED BY | R.Saban, R.Schmidt, M.Vanden Eynden with help of L.Tavian | VALIDATED BY | Not validated yet |
| RELATED DOCUMENTS | - UML Sequence Diagram - Dipole Powering Circuit of String 2 : http://wwwlhc01.cern.ch:8050/lhc_proj/owa/lhcp.page?p_number=6760 |

## DESCRIPTION

| PURPOSE | Study : flow of information in case of a dipole magnet quench and diagnostic and recovery procedures for bringing LHC back in operational state |
| --- | --- |
| ASSUMPTIONS & SIMPLIFICATIONS | Machine @ nominal Energy and beam intensities All Logging processes active for Power Converters, Quench Protection System and Cryogenics |
| ACTORS | Power Converter, Operator |
| USES | “Diagnose LHC Magnet Quench” use case “Recover from LHC Magnet Quench” use case |

## TYPICAL COURSE OF EVENTS

Use case starts when :

[1] A failure occurs in a 600A LHC Power Converter feeding some sextupole magnets

[2] beam starts oscillating (beam blow-up is another possibility)

[3] Beam loss occurs at time t=t0

[4] A dipole magnet (not the one located at the end of a LHC cell – see later for quench propagation) quenches

[5] After a few milliseconds [TBD] depending on the integration time of the beam loss monitors, the loss is effectively detected by the beam loss monitor system

[6] beam loss monitor system sends a “Beam Abort” signal to the LHC beam dump system which in turn dumps the beam (within 1 turn). If beam not dumped after t0 + 20msec, then beam will hit the collimators.

[6] At t=t0 + 20msec, the quench protection system has detected the quench (V in dipole ~ 200 mVolts) and : fires the dipole heaters after a validation time of ~10 msec (to avoid false alarms) raises a “PowerAbort” signal which is sent to the Dipoles Power Converter(s) and to all other magnet powering circuits in the concerned LHC cell (QF, QD, …) opens the energy extraction switch of the Dipoles powering system (all dipoles in serie) informs several external systems including some SPS systems, the LHC operator and the LHC Experiments [ list not exhaustive and TBC]

[7] At reception of the “Power Abort” signal, the control system sends a “Freeze Logging” message to the Power Converters, Cryogenics and Quench Protection loggers in order to freeze the image of their circular logging buffers. This facility is mandatory for the post mortem analysis of the quench.

[8] At t =t0 + 50msec, the dipole magnet heaters become effective and the He pressure increases

[9] At t=t0 + 150msec, the He relieve valves of the dipole magnet open (Pressure >= 20 Bars)

[10] Cryogenics system has detected the quench and removes the “Power Permit” for the concerned LHC sector in order to prevent the re-powering the magnets which have quenched (this system will raise a “Power Permit” at the end of the quench recovery – see “Recover form LHC Magnet Quench” use case)

[11] At t=t0 + 104sec, the current in the dipole magnet is ~ 0 (time constant of the L,R discharge circuit for all dipoles in the concerned LHC arc)

[12] At t=t0 + n*10sec (n TBD), the quench propagates to the 2 adjacent LHC magnets

[13] Temperature in the quenched magnets are ~ 30K and Pressure decreases

[14] USE CASE “Diagnose LHC Magnet Quench” starts now

[15] USE CASE “Recover from LHC Magnet Quench” starts now

Use case ends when LHC is operational for next injection

## ADDITIONAL INFORMATION

| NOTES | A quench may propagate in the worst case in to 4 LHC cells Cryogenics System : This system is able to detect quench situations by its own through : Temperature measurements in each magnet (T ~ 30K after a quench) Pressure measurements in specific circuits which can inform about the quench intensity (Pressure ~ 3 Bars for a limited quench) A failure of 1 Power Converter is realistic, but failures of a complete set of Power Converters (Main electrical failure) is also most likely to happen Quench protection system : This system can provoke a dipole quench in 2 cases : After a loss of power in one magnet protection system (redundant UPS available) After a “false” quench detection |
| --- | --- |
| OPEN ISSUES | The exact list of systems and signals to be sent in [6] has to be clarified : Should some particular SPS systems be signaled ? which ones ? The operator must be informed. How ? Alarm display ? |

##### 2.  Related LHC Control System Requirements

| NEED FOR A LHC INTERLOCK MANAGEMENT SYSTEM | 1. The “Power Abort”, “Beam Abort” signals in [6] must be transported through an interlock management mechanism of the LHC control system which has the following constraints : Reliability : 100% Availability : 100% of machine operation time Response time : < 20 msec [TBC] 2. The “Power Permit” signal set/unset by the cryogenics system has to be processed by a non-critical software interlock management mechanism of the LHC control system 3. There is a need |
| --- | --- |
| LHC OPERATIONAL EVENTS DISTRIBUTION SYSTEM | Most LHC systems will log their status information in so called “circular buffers” with a limited time window. There is a need, under several operational conditions, to ask these systems to “freeze” their logging process in order not to loose important data related to a quench situation and to transmit this data up in the control system for post mortem diagnostics. Typical operational events that could be distributed for freezing logging processes are : Beam aborts Power aborts |

3. Communication between Core Systems – Sequence Diagram

4. Sequence of Logging Events (in view of the Quench Post-Mortem Diagnostic)